## Intro
Stage 0 PDUP Checklist
Version: | 1
Date: | 2024-04-02
Overview: | This PDUP Checklist has been prepared to aid market participants with their model submissions and to outline model practices of the AESO. The AESO plans to continually improve and enhance the PDUP Checklist in the future as necessary.
Instructions: | As part of the PDUP Model submission complete a review each the three RAW, SEQ, and DRY files using the corresponding sheets in the PDUP Checklist. The PDUP Checklist spreadsheet will be submitted to the AESO as part of the model package. Each Parameter specified shall be compared to its Check and Confirmed. The confirmation of each parameter shall be entered into the PDUP Checklist. Where a parameter is outside typical ranges or doesn't align then Rational shall be provided in the PDUP Checklist.
Disclaimer: | While the AESO has made significant effort to ensure this checklist is accurate, it is not guaranteed and market participants are still accountable to ensure their submitted models are correct. Please notify the AESO of any issues so they can be investigated. The AESO plans to continually improve and enhance the PDUP Checklist in the future as necessary.
Alignment: | In general, if there are inconsistencies between this PDUP Checklist and the "Project Data Update Package - Instruction Manual" (PDUP-IM) the PDUP Checklist will take precedence as it reflects more recent practices and the latest released requirements.
Prepared by: | Khalid Rafiq, Nima Safari, Visu Viswanathan, Stephen VanderZande, Yvonne Hong, Engy Hassan, Cindy Fung.
Comments or issues with the PDUP Checklist can be emailed to customer.connections@aeso.ca.

## RAW
Stage 0 PDUP Checklist | VERSION 1
RAW Data Check
Parameter Group | Parameter | Check | Stage 0 (Cluster) | Confirmed (Y/N) | Rational (as required)
Information | PSS/E Version No. | Required at start of the file. Version 34 or greater required. (e.g "VERSION 34") | √
| RDCH | Required command line. | √
| 1 | Required after RDCH. | √
| Q | Required at the end of file. | √
Bus Data | I | Check bus numbers. For Connection Projects, temporary bus numbers are used unless permanent bus numbers are already assigned (e.g BTF where some buses already exist). Temporary bus numbers shall be in the range of 990001 to 999001. | √
| Name | Bus name is required and entered using the bus number (temporary or permanent) followed by _1, _2, etc.. For example, when using temporary bus numbers the names may be 99000_1 and 99000_2 based on the bus numbers used. | √
| BASKV | Bus nominal voltage in kV is required. Nominal voltage on transmission side are 500 kV, 240 kV, 138 kV and 69 kV. | √
| IDE | Bus code of 1 for load bus and 2 for generator bus (including ESR). | √
| Area | Area number is required and should not be 9999 | √
| Owner | Owner number is required for existing facilty. For a new facility can be left at default value. | √
Load Data | I | Check that load is modelled at the correct bus location. | √
| ID | Load ID is required using NAICS code. (e.g. 32, 99 etc.) Refer to the NAICS Industry Description Codes table found in the PDUP IM. | √
| AREA | Area number is required and should not be 9999 | √
| PL, QL | Active and reactive component of load is required. It should be equal to DTS (except for Industrial System Designation (ISD)). | √
| Owner | Owner number is required for existing facilty. For a new facility can be left at default value. | √
| SCALE | Set to 1 for scalable and 0 when a fixed load. | √
Machine | I | Check that machine is modelled on the correct bus location. It should be consistent with SEQ and DYR files. | √
| ID | Machine ID is required. For transmission connected, ID should be G1, G2 etc. For DERs, ID should be D1, D2 etc. This ID must be consistent with SEQ and DYR file. | √
| PG | For single or independent conventional machines and IBRs, Pgen should be set equal to Pmax to get the required MARP. For hybrid facilities refer to the AC Coupled SLD and DC Coupled SLD. | √
| QT | Lagging PF must be at least 0.9. Anything greater than 0.88 provide rational. For T-connected Inverter-Based Resources (IBRs), based on point of connection per "AESO Connection Requirements for Inverter-Based Resources". For conventional machines, based on the machine (stator) terminal bus. | √
| QB | Leading PF must be at least 0.95. Anything greater than 0.93 provide rational. For T-connected IBRs, based on the point of connection. For conventional machines, based on the machine (stator) terminal bus. | √
| VS | Voltage setpoint for regulated bus. It should be from 0.95 to 1.05. | √
| IREG | Bus number should be 0 if using terminal bus (e.g. for conventional machine). Otherwise enter bus number used for voltage regulation (e.g. for T-connected IBRs the point of connection per the "AESO Connection Requirements for Inverter-Based Resources"). | √
| MBASE | For IBRs, it is total installed capacity from inverter nameplates. For conventional machine, it is machine MVAbase from nameplate. | √
| Impedance | For IBRs, typical range of sub-transient reactance Xd" 0.5 to 0.8 is acceptable. For conventional machines, typical range of sub-transient reactance Xd" is 0.18 to 0.22 is acceptable. | √
| PT | For conventional machines Pmax is the generator output at stator terminal and equal to MARP. For IBRs, Pmax = MARP + Losses (GSU and collector system) For hybrid facilities refer to the AC Coupled SLD and DC Coupled SLD. | √
| PB | For IBRs and conventional machines set to minimum generator output. For Energy Storage Resources (ESR) it is the charging level from the system entered as a negative value. | √
| Oi | Owner number is required for existing facility. For a new facility can be left at default value. | √
| WMOD | Control mode '0' is used for conventional machines. Control mode '1' is used for transmission connected IBRs. Control mode '3' is for fixed reactive power used for DER IBRs. | √
| WPF | Only required for DER IBRs when WMOD is '3' as the wind power factor to calculate reactive power. | √
Distribution feeders 25 kV, 13.8 kV etc. or collector system for IBR | I, J | Check to and from bus numbers. It should be consistent with SEQ and DYR file. | √
| CKT | For a distribution feeder, CKT id is the last two digits of the line number (e.g. 2035L -> 35). For collector system of IBR, CKT id should be L1, L2, etc. considering numbering for any existing lines at that facility. | √
| R, X and B | R, X and B should be P.U. R/X ratio depends on conductor and should be in reasonable range. | √
| Name | For existing distributions lines name of line is required (e.g. 2035L). For new distribution lines, no name required. For an existing facility, name shall be facility code (e.g. 9999S) followed by L1, L2, etc.. (e.g. 9999SL2) consistent with the CKT Id. For new collector system facilities, no name required for feeders part of the collector system. | √
| Rating | Summer, Summer emergency, Winter, Winter emergency. All four ratings are required. | √
| LEN | Length of the distribution feeder from the DER connection point. Feeders in IBRs is represented as collector system so length is not required. | √
| Ownership | Owner number is required for existing distribution feeders. Owner number of collector system for IBRs are required when facility codes are assigned at stage 3. | √
Transmission Line |  | Transmission Line not required in Stage 0 PDUPs. | √
Transformer | I, J | Check bus numbers correspond to correct location. | √
| CKT | Ckt ID needs to be provided. It should be T# | √
| CW | It should be 1 | √
| CZ | It should be 1 | √
| CM | It should be 1 | √
| MAG1 (G) | Magnetizing admittance needs to be entered. | √
| MAG2 (B) | Magnetizing conductance or susuptance needs to be entered. It will be negative value. | √
| NAME | Transformer name is not required at stage 0. | √
| Oi | Owner number is required for existing facility. For a new facility can be left at default value. | √
| VECGRP | Vector Group is required. It should be consistent with connection code (CC) in SEQ file. | √
| R, X | R and X should be in P.U. based on 100 MVAbase. R and X values outside range of 7 % to 14 % require rational. X/R ratio will depend on the transformer size. For additional information please refer to figure 1-44 in the AESO's Transformer Modelling Guide (https://www.aeso.ca/assets/linkfiles/4040.002-Rev02-Transformer-Modelling-Guide.pdf) | √
| MBASE | Transformer impedance should always be on 100 MVA base | √
| WINDV1 | It is 1, if rated and nominal kV is same. | √
| NOMV1 | Nominal voltage of winding 1 in kV. | √
| Ratings | Three or more ratings are required for each transformer. GSU transformer ratings must be equal or greater than generator MVA. The interconnection transformer rating should be greater than MARP/0.9 MVA. ISDs and self-supply cases may indicate rational for smaller interconnection transformer ratings. | √
| COD1 | Tap changer type is 0 for an off-load tap changer and 1 for an on-load tap changer. Typically 0 for GSU transformers and 1 for interconnection and load transformers. | √
| CONT1 | For conventional GSU transformers, regulated voltage bus number is normally not required since voltage is regulated by machine. For IBRs, regulated bus numbers is high side of interconnection transformer. For load transformers, regulated bus number is required. | √
| RMA1, RMI1 | Tap ratio upper and lower limits. Required and depends on rated and nominal kV of transformer. | √
| VMA1, VMI1 | Required upper and lower limits of the regulated bus. If COD1 is 0 then it is not required. Refer to the 503.4 and the IBR Requirements for ranges. | √
| NTP1 | Number of taps GSU transformer are normally 3 or 5. For IBR interconnection transformer and load transformers, it is normally 17, 25, 33 or depends on tap changer. It should not be 9999. | √
| WINDV2 | It is 1, if rated and nominal kV is same | √
| NOMV2 | Nominal voltage of winding 2 in kV | √
Areas, Zones and Owners | Areas, Zones | No new Area or Zone data should be entered. | √
| Owners | Owner data to be provided only when there is a new owner. | N/A

## SEQ
SEQ Data Check
Parameter Group | Parameter | Check | Stage 0 (Cluster) | Confirmed (Y/N) | Rational (as required)
√
Information | PSS/E Version No. | Required at start of the file. Version 34 or greater required. (e.g. "VERSION 34") | √
| RESQ | Required command line. | √
| 1 | Required after RESQ. | √
| Q | Required at the end of file. | √
Machine | I | Check bus number such that machine is modelled on correct bus. It must be consistent with RAW and DYR files. | √
| ID | Machine ID must be consistent with RAW and DYR file. For example G1, G2 or D1, D2. | √
| Impedance | For IBRs, typical range of sub-transient reactance Xd" 0.5 to 0.8 is acceptable. For conventional machines, typical range is 0.18 to 0.22 is acceptable and Xd"<Xd'<Xd. | √
Distribution feeders 25 kV, 13.8 kV etc. or collector system for IBR | I,J | Check to and from bus numbers. It should be consistent with RAW file. | √
| CKT | Ckt id must be consistent with RAW file. | √
| R, X and B | R, X and B should be P.U. R/X ratio depends on conductor parameters and should be in reasonable range. | √
Transformer | I,J | Check bus numbers are consistent with RAW file | √
| CKT | Ckt ID must be consistent with RAW file. | √
| CZ0 | It should be 1 | √
| CZG | It should be 1 | √
| CC | Connection code (CC) should be consistent with vector group in RAW file. It shall be modelled as two winding transformer unless clear need to model as three winding, which must have rational provided. Typical interconnection transformers and CC include: - YgYg with delta tertiary: CC = 18 (usual for IBRs) - DYg: CC=13 (usual for loads) - YgD: CC=12 (used for some conventional machines) - DYg with grounding transformer: CC=17 (used by DER for effective grounding) For other options refer to PSSE Program Operation Manual for full list of CCs. | √

## DYR
DYR Data Check
Parameter Group | Parameters | Check | Stage 0 (Cluster) | Confirmed (Y/N) | Rational (as required)
|  | Note that dynamic model quality test requirements, testing tool, and guidelines will be release by the AESO in the future. | √
|  | Only WECC approved models shall be used with the latest list available here: | √
|  | https://www.wecc.org/Pages/results.aspx?k=approved%20dynamic%20models | √
Machine Bus Number | IBUS | Bus number should be consistent with RAW and SEQ files. | √
Machine ID | ID | Machine ID should be consistent with RAW and SEQ files. | √
√
REPCA1 | Bus Number (M) | For transmission connected Inverter-Based Resources (IBRs), based on point of connection per "AESO Connection Requirements for Inverter-Based Resources". For DER IBRs that operate in fixed PF mode it is not required. | √
| (M+1) to (M+4) | To and from bus numbers required along with CKT id. | √
| (M+5) Voltage control | For transmission connected IBRs shall be 1. For DER IBRs that operate in fixed PF mode it shall be 0. | √
| (M+6) Frequency Control | Refer to requirements of the "AESO Connection Requirements for Inverter-Based Resources". | √
Protection models (e.g. VTGTPAT, FRQTPAT) |  | Protection models are to be included and they must be loadable into PSSE. Parameters should consider requirements of ISO Rules and IBR Connection Requirements. | √

## Typical SLD
DER | IBRs | Conventional

## Hybrid SLD
Hybrid facility (DC Coupled) | Hybrid facility (AC Coupled)
Note: The SLD is an example of DC coupled hybrid facility. When a source (typically solar) and an ESR are connected on DC side (DC Coupled) such that they share inverters, it should be represented as one generator G1. Pmax should be adjusted to get required MARP value at collector bus. Typically the ESR is charged from the other source such that Pmin will zero, otherwise Pmin should reflect system draw. | Note: The SLD is an example of AC coupled hybrid facility. When two sources are connected on AC side (AC Coupled), it should be represented as two generators (e.g. G1 and G2). There may be a shared or separate transformers. For conventional machines, Pmax for each machine should be maximum generator output adjusted to provide MARP at stator terminal. For IBRs, Pmax for each machine should be maximum generator output adjusted to provide their defined MARP value at their collector bus. If an STS or other limitation for the combined output is present, then Pgen for each machine shall be adjusted using a weighted value.
AC Coupled Examples
Assuming Source 1 MARP 200 MW, Source 2 MARP 200 MW and no losses in the collector system.
ESR only charging from coupled source.
Source 1: Pmax = 200, Source 2 (ESR): Pmax = 200 Pmin = 0
ESR also charging from system.
Source 1: Pmax = 200, Source 2 (ESR): Pmax = 200 Pmin = system draw
Single asset - two sources limited by STS or other limitation (300MW).
Source 1: Pmax = 200 Pgen = weighted value of limitation = 150 MW, Source 2: Pmax = 200 Pgen = 150 MW.