## Process
| PJM | ISO-NE | NYISO | MISO | UK (National Grid)
Type of load forecasted | -Non-coincident and coincident monthly peak load by energy zone after reductions for distributed PV and prior to reductions for load management impacts or voltage reduction. -Locational deliverability area peaks (i.e. by capacity zone) -Summer 90/10 peak (extreme weather peak; 90% probability of more moderate weather and 10% probability of more extreme) -Winter 90/10 peak (extreme weather peak; 90% probability of more moderate weather and 10% probability of more extreme) -Total net energy (MWh) forecast -PV capacity forecast -Load management forecast | ISO-NE forecasts monthly peaks and annual energy. ISO-NE develops a gross and a net forecast, wherein the gross forecast reconstitutes behind-the-meter PV and passive demand response. | For capacity procurement purposes, NYISO forecasts coincident peak load and also peaks for each capacity market zone.Capacity zones include New York City, Long Island, and Lower Hudson Valley. Capacity Zones have a minimum quantity of supply that must be sourced locally. The locational capacity requirements account for local peak load, minus the quantity of imports expected at peak, plus the additional supply needed to meet reliability criteria. | Coincident peak demand on a system-wide basis. For each capacity zone, MISO uses forecasts zonal peak load that is coincident with system peak and non-coincident with system peak. | Forecast is of "Unrestricted National Demand" which is The amount of electrcitiy supplied from grid supply points (points of entry from the transmission to the distribution system) + energy supplied by embedded large power stations (i.e. behind the meter distributed resources) + Transmission losses - Demand taken by station transformers and pumped storage uses Note that exports are not counted as demand in the forecast
| [Source 4] | [Source 1, page 6] | [Source 2, page 1-2] |  | [Source 1, page 37], [Source 5, page 28]
Frequency of forecast | The base forecast used for the capacity market is published on an annual basis, typically in January, with a summer update, typically in July. PJM shares a draft of the forecast in the fall. | The forecast is conducted on an annural basis and posted in May. It is posted as part of the Capacity, Energy, Loads, and Transmission (CELT) report. | Annual | Annual | Annual
| [Source 1, Page 13] | [Source 2] | [Source 2, page 1-1]
Who approves methodology? | PJM conducts a stakeholder process and ultimately has its methodology endorsed by the Markets and Reliability Committee, composed of PJM members. | ISO-NE staff have the primary role in developing the methodology. ISO-NE will also take input from the Load Forecasting committee which is made up of stakeholders including municipalities, transmission owners, and energy suppliers. | NYISO's Business Issues Committee has an Installed Capacity Working Group which has designated the Load Forecasting Task Force with preparing and presenting the forecast used in the capacity market. The Executive Committee then approves input assumptions for calculating the reserve margin. | Loss of Load Expectation Working Group (reports to Resource Adequacy Subcommittee) | The Panel of Technical Experts oversees the process. There is also a robust stakeholder involvement. Inside National Grid, the process is overseen by the Director of UK System Operation.
| [Source 1, page 23] | [Source 5] | [Source 2, page 1-1] | [Source 1] | [Source 1, page 32]
How are load forecasts used? | PJM generates forecasts for all PJM zones (of which there are 20) and publishes its annual forecast in January of each year. In general, load forecasts are used to set targets in PJM's Reliability Pricing Model, which is PJM's capacity market mechanism. Specifically, what is fed into the Reliability Pricing Model is coincident peak load, netted of distributed PV, but not adjust for demand response.The forecast is also used to support the Regional Transmission Expansion Plan along with other reliability studies which PJM may elect to conduct. The energy forecast is used in reporting requiresments for the Federal Energy Regulatory Commission and the North American Electric Reliability Corporation, and for efficiency studies which PJM may elect to conduct. PJM provides data so that stakeholders can review the forecast. Historically, PJM shareholders have lobbied PJM to change its methodology when PJM's forecasts prove inaccurate. PJM has responded by making changes to the methodology to address historical accuracy issues. Such changes go through a stakeholder process. The most recent significant change has been in 2015 when PJM chose a more granular approach to how energy efficiency and distributed PV are considered in its methodology. PJM completely reformed its approach to address an over-forecasting bias. | Load forecasts feed into the annual CELT report and are used to determine the necessary supply to be targeted in ISO-NE's capacity market, as well as the transmission planning process. | The load forecast is used in the calculation of the resource adequacy requirement New York Control Area and each capacity zone. Long-term forecast is also used for transmission planning and NERC reporting. | The forecast is used to set system-wide and locational capacity requirements for MISO's capacity planning resource auction, which occurs in March for the planning year starting in June. Longer-term load forecasts are used in MISO's transmission planning process, NERC reporting, and for other studies. | Forecasts are fed into National Grid's "Least Worst Regret" model. The Least Worst Regret model optimizes the capacity procurement by considering the value of lost load and also the cost to procure capacity. The output determines the capacity requirement in the capacity market.
| [Source 1, page 13] |  |  |  | [Source 1, page 104]

## Approach
| PJM | ISO-NE | NYISO | MISO | UK (National Grid)
Approach to model (bottom-up, top-down, econometric) | Bottom-up econometric regression. Regressions are conducted for PJM energy and capacity zones and then aggregated | Bottom-up econometric regression. ISO-NE uses an iterative process wherein annual energy load is forecasted and then fed into a peak forecast model. The economic/demographic control for the peak load forecast is embedded in the input form the energy forecast. | NYISO has two primary load forecasts. The first is a near-term (first year) load forecast which is used for NYISO capacity market procurements. This forecast primarily relies on the reported forecast data from transmission owners and municipal electric systems. To calculate the NYISO peak load, NYISO takes the previous year's adjusted actual peak load in each locality, adjusted by the regional load growth factors for the upcoming year. Adjusted actual load includes load adjusted to reflect: (i) Load relief measures such as voltage reduction and Load Shedding; (ii) Load reductions provided by demand side resources; (iii) normalized design weather conditions; (iv) station power delivered that is not being self supplied; and (v) adjustments for special case resources and emergency demand response. Regional load growth factors are provided by transmission owners and municipal electric systems. Regional load growth factors represent the year-over-year growth in weather-normalized coincident peak load for the respective territory of the transmission owners or municipal electric system. This near-term forecast for capacity procurement is the forecast which is described in the rest of this document (unless otherwise specified). The other primary load forecast NYISO also conducts a long-term forecast used for long-term studies and transmission planning. It is published in NYISO's annual "Gold Book," which is NYISO's report of Load and Capacity data. For the Goldbook, NYISO conducts a baseline forecast, which includes impacts of energy efficiency, building codes, and distributed energy generation. It also conducts an econometric forecast which accounts for economic change. The first year of the long-term forecast is adjusted to match the near-term forecast used for capacity planning purposes, but otherwise uses an entirely separate methodology. | MISO has two load forecasts: (1) load-serving entites' self-forecasts aggregated to the system level used for capacity market and most other purposes, and (2) an independent top-down forecast used as an independent accuracy check (planned only for three years, not permanent). This document refers to the bottom-up LSE self-forecasts except where otherwise noted. LSE self-forecast: Load serving entitites (and in retail choice zones, the electric distribution companies (EDCs)) submit non-coincident and coincident peak demand forecast and monthly peak demand forecasts, which MISO applies to historic load shapes to develop estimates of zonal and system coincident peak. LSEs/EDCs also submit documentation on the methodology used to arrive at their demand forecast. MISO draws a random sample of 20 load serving entities to assess and validate the processes. Independent forecast: top-down econometric model, state level and system level. | Annual energy demand is first forecasted, and then a ratio for the relationship of annual energy demand to peak demand is applied. Annual energy demand: Annual demands are broken into four categories for modeling: Domestic, industrial, commercial, and other/sundry. Domestic: Domestic demand uses a bottom-up approach where components are separately forecasted and aggregated. Components include appliance, resistive heat, resistive hot water, lighting, domestic annual demand reduction (smart meter effect), heat pumps, and electric vehicles. Industrial and Commercial: National Grid has worked with Arup and Oxford Economics to develop a modular model with three basic components: 1) Macro-economic long-term forecasts 2) Energy demand based on economic activity, prices, and temperature 3) Technology investment Other/sundry: There is not a specific formula for other/sundry. The category represents other line items such as losses and micro-generation Peak demand: Once annual energy demand is created, a recent historical relationship of annual energy to peak demand is applied. This creates a base. On top of this base, peak demand components which history cannot predict (due to newness) are overlaid. These components include electric vehicles, heat pumps, micro-generation, losses, and demand response.
| [Source 3, page 9] |  | [Source 1, page 1] [Source 2, page 1-2] | [Source 2, page 26] | [Source 1, pages 38-40]
Why was the approach chosen and what software is used | PJM has used an econometric approach since its first load forecast in 2006. However, over time, PJM has made significant changes to its approach in response to feedback from stakeholders. Beginning with the Great Recession, the accuracy of PJMs model decayed. As the recession eased, it became clear that the inaccuracies of the PJM forecast were driven not just by the recession, but by other changes inside PJM. Notably, PJM was not adequately accounting for distributed energy resources and energy efficiency gains per unit of GDP. In 2015, PJM conducted a significant overhaul of its load forecast methdology. It began to directly incorporate energy effiency and distributed generation (as discussed in the "Inputs" matrix). The software PJM uses is SAS. For resource adequacy calculations, PJM uses GE-MARS (for system requirements) and an in-house tool PRISM (for locational requirements) | ISO-NE's approach has changed over time and reflects stakeholder feedback with respect to methdology. For calculating the reserve margin target (given the load forecast as an input), ISO-NE uses GE-MARS. | The approach was chosen after an iterative stakeholder process. For resource adequacy calculations, NYISO uses GE-MARS. | LSE Forecast: MISO has conducted a number of stakeholder processes to develop this methodology. The decentralized approach reflects the historical and regulatory context in which vertically integrated utilities in the footprint have primary responsibility for integrated resource planning. For resource adequacy calculations, MISO uses GE-MARS. Independent Forecast: uses the best judgement of the independent forecasters. Software: EViews. | Each year, National Grid has a stakeholder process where stakeholders submit feedback. This is part of the Future Energy Scenario process, which is closely related to National Grid's foecast for capacity planning/procurement purposes. National Grid has worked with statekholders over time to come to its current methodology.
| [Source 3, page 15] |  |  |  | [Source 1, page 38]

## Inputs
8
| PJM | ISO-NE | NYISO | MISO | UK (National Grid)
Area (subregion?) | Most granular forecast is by energy or capacity zonelLocational deliverability area (PJM has 20 energy zones and 15 capacity zones). Locational deliverability areas can be energy zones, sub-regions of energy zones, or a collection of energ zones. An RTO-wide forecast is also produced. | Forecast is conducted for each state and also for ISO as a whole | Forecast is reported for localities in NYISO and NYISO as a whole. Relevant localities include New York City, Long Island, and Lower Hudson Valley. Localities have separate requirements from the rest of NYISO. | MISO presents aggregate data on a system-wide basis and by capacity zone, though the load serving entitites and electric distribution companies submit data for their respective territories. | UK as a whole
| [Source 1, page 13] | [Source 1, page 7] | [Source 4, page 17]
What inputs (e.g. economic, historical load, weather) and what granularity | "The model uses trends in equipment and appliance usage, anticipated economic growth and historical weather patterns" | ISO-NE runs separate models for the peak and annual energy forecasts. The annual energy forecast is modeled as a function of economic and other drivers. It is then used in the peak model to represent economic/demographic effects. Once the annual energy forecast is completed, it is processed further to generate annualzed monthly moving sum values, which are fed into the peak model. To generate the monthly moving sum value, the monthly moving sum is calculated for the latest historical year by calculating the sum of net energy for each month and the 11 previous months. Net energy is then calculated for the latest historical year and annual growth rates are calculated. The growth rates are applied the the monthly moving sums, which creates the input for the peak model. The fundamental inputs of the Energy model are as follows: - Historical load reconstitued for passive demand response and distributed PV; sample period is 1990-2016 for the 2017 forecast cycle - Economic activity represented by Gross Regional/State Product - Energy price adjusted for inflation - Weather represented by Annual Heating Degree Days and Annual Cooling Degree Days based on the temperature-humidity index. - Binary variables for specific years The fundamental inputs of the Peak model are as follows: - Output from the Energy model, discussed above - Weather represented by weighted temperature-humidity index for May-Sept and drybulb for Oct-April - Time trend, day effects (weekends, holidays) | For capacity planning purposes (near-term forecast) transmission owners and municipal electric systems submit to the ISO: 1. Hourly loads for each quarter (first quarter is January – March, etc.) within 90 days after the quarter’s end; 2. Actual load during the hour and on the date of the New York system peak, and including a statement of whether or not transmission losses are included ; 3. The weather-normalized load during the hour and on the date of the New York peak 4. The previous five years’ values for #2 and #3. 5. The MW impact of Emergency Operating Procedures and load modifiers operating during the hour and on the date of the New York peak; 6. For TOs with Locational Minimum Unforced Capacity Requirements, the actual and weather-normalized Locality noncoincident peak load; 7. Regional Load Growth Factors. With this information, NYISO does the following: 1. Reconcile reported coincident peak loads by comparing reported load to billing data. 2. Calculates load less losses. Losses are obtained from the ISO database. 3. Deduct station power 4. Evaluate tranmission owner and municipal electricity system weather normalized load and losses. NYISO does this by conducting its own calculations for the weather-normalization of load. If NYISO-calculated weather normalized load and losses are close to that provided by transmission owners and municipal electricty systems, then NYISO accepts the inputs (thus deferring to the calculations conducted by the transmissions owners and municipal electricity systems). If the values significantly differ, NYISO will work with the individual entity to reconcile the difference. 5. Allocate weather-normalized losses to tranmission owners and municipal electricity systems. NYISO does this by allocating weather-normalized losses according to the ratio of each area's load less losses and the New York's load less losses. The sum of all the allocated weather-normalized losses + load for all transmission districs is equal to the New York weather-normalized peak load. 6. Evaluate Regional Load Growth Factors. Regional Load Growth Factors are initially provided by transmission owners and municipal electricity systems. NYISO develops ranges based on historical peak load growth, economic growth, and its own expectations of year-over-year growth. NYISO accepts Regional Load Growth Factors which fit into its ranges, and works to reconcile Regional Load Growth Factors outside of those ranges. 7. Forecast of coincident peak, calculcated as (weather normalized load + losses) * Regional Load Growth Factor 8. Forecast locaility peaks, similar to how coincident peak is forecasted, but with non-coincident peak load. The longer-term forecast conducted by ISO-NE uses a different methodology relying on economic variables and accounting for policy programs. | Load serving entities are allowed to incorporate any variables they choose when developing their own peak load analyses to MISO. As such a wide variety of techniques and inputs are used. MISO has provided best practices guidance indicating that end-use, econometric, and hybrid forecast approaches are acceptable as long as they rely on explanatory variables such as electricity prices, economic variables, weather, and end use data. MISO has identified other approaches including time trend and autoregressive approaches as unacceptable based on the lack of reliance on explanatory variables. | As discussed in the "approaches" section, National Grid conducts bottom-up modeling. Each sub-module is comprised of different controls. In general, National Grid utilizes 10 years of historical demand. National grid models economic drivers in separate modules. Weather is also included (discussed below). National Grid also includes controls for a number of other factors, including number of homes, population, fuel prices, energy storage costs, product turnover.
| [Source 1, page 13] | [Source 1, pages 5-7] | [Source 2, pages 2-2 - 2-7] | [Source 2, page 26] [Source 3] | [Source 2]
How is the economic control determined? | Economic controls include: residential sector sales share; commercial sector sales share; industrial sector sales share; number of households; population; real personal income; non-manufacturing employees, U.S. gross domestic product, area gross metro product. The economic vendor is Moody's Analytics | In the energy model, the economic control is represented by Gross Regional/State Product adjusted for inflation. It is from Moody’s Analytics. Gross domestic product is adjusted for inflation by Moody’s price deflator series. In the Rhode Island model, real personal income is used instead. In the peak model, monthly moving sum net energy, derived from the energy model, is used as an economic and demographic control. | For capacity planning purposes (near-term, one-year load forecast), NYISO does not incorporate an economic control. However, as discussed above, NYISO does utilize some economic indicators to evaluate regional load growth factors provided by transmission owners and municipal electric systems. NYISO considers the ratio of historical load growth to growth in economic indicators for the previous five years and the current year. The selection of economic indicators is conducted by the Load Forecasting Task Force. | MISO does not independently incorporate an economic control. This is left to individual load serving entities to decide. However, MISO does require that the LSEs/EDCs submit a load forecast consistent with "average" economic conditions (rather than a high or low economic forecast). | The economic data are from Oxford Economics. The model uses a bottom-up approach wherein data are forecasted for 24 sub-sectors and then aggregated.
| [Source 1, page 22]; [Source 4, page 1] | [Source 1, page 7, 12] | [Source 2, page 2-4, 2-6] |  | [Source 2, page 43]
How is weather considered and modelled? | PJM forecasts weather-normal (50/50) peaks along with extreme weather peaks (90/10). PJM uses a Monte Carlo approach which varies future weather conditions based on weather observed over many previos years. This produces a distribution of monthly forecasts, where the median result is the base forecast (50/50) and the 10th percentile and 90th percentile are assigned to extreme (90/10) scenarios. Heating and shoulder seasons (Jan-Apr and Oct-Dec) and cooling and shoulder seasons (March-Nov) have different controls. For the heating and shoulder seasons, "wind speed adjusted dry bulb temperature" (WWP) is used. For the cooling and shoulder seasons, THI is used. Each is define as follows: WWP: If wind speed > 10 mph, WWP = drybulb - (0.5 * (wind speed - 10)) If wind speed <1 mph, WWP = drybulb THI: If drybulb > 58, THI = drybulb - 0.55 * (1 - relativehumidity) * (drybulb - 58) If drybulb < 58, THI = drybulb PJM also incorporates Heating Degree Days and Cooling Degree Days | In the energy model, weather is represented by two variables: Annual Heating Degree Days and Annual Cooling Degree Days based on the temperature-humidity index. In the peak model, weather is represented by two variables: weighted temperature-humidity index minus 55 for May-September, and 65 minute dry bulb temperature for October-April. Note that weighted temperature-humidity index is a 3-day weighted temperature-humidity index. The temperature-humidity index utilized by ISO-NE is calculated as .5 * drybulb temperature + .3 * dewpoint + 15. | For capacity planning purposes, NYISO requires that the forecast be consistent with a normal 50/50 weather year. This means that transmission owners and municipal electric systems are required to normalize historical load and report on their methodology, and then apply load growth factors to normalized load data. NYISO also calculates its own weather-normalized peak load for each submitted forecast as a check for consistency. In the long-term forecast, NYISO estimates a peak load forecast for summer and winter in the 10/90, 50/50, and 90/10 weather years. | MISO does not independently incorporate weather data, this is left to individual load serving entities to decide. However, MISO does require that the LSE/EDC forecasts are consistent with a "weather normal" year, i.e. the 50/50 weather year. MISO does develop estimates of load forecast uncertainty for use it its LOLE study (see outputs tab). | Demand is weather-normalized. In general, National Grid uses 10 years of historical data. National Grid includes a cold recent winter as a cold weather sensitiivty. Wind speed is considered separately, and 36 years of historical wind speeds are considered to create a distribution.
| [Source 1, page 14]; [Source 3, page 15] | [Source 1, page 7, 12] | [Source 2, page 2-4] | [Source 2, page 26] | [source 1, page 23,31]
How are distributed energy resource (DER) projections created and accounted for? | DERs are forecasted separately and used to adjust the load, with separate accounting for DERs that are not qualified to sell capacity (used to adjust peak load used in the capacity auction) vs. those that are not qualified to sell capacity (indicative forecasts only). Demand Response (indicative, capacity qualified): Demand Response is based on the PJM final summer season committed DR (DR committed through the capacity market). To create a forecast, PJM computes the total comitted DR for the three most recent delivery years and expresses this number as a percentage of the zones 50/50 forecast summer peak. Each zone's DR forecast is equal to the zone's 50/50 summer peak multiplied by the three-year average committed DR percentage. Distributed PV (not capcaity qualified, used to net forecast into capacity auction): PJM accounts for distributed solar with a bottom-up, out-of-model solar forecast. PJM first back-casts historical distributed solar generation to so that the model more accurately estimates the relationship between load and other variables. PJM uses historical weather controls for the back cast. This includes cloud cover data from National Oceanic and Atmospheric Administration and temperature data. PJM also utilizes tilt and DC to AC conversion factors from the National Renewable Energy Laboratory PVWATTS simulations. Once this is all complete, PJM adjusts historical load data to generate a forecast which removes the impacts of distributed solar. PJM then works solar projections into the long-term forecasts. PJM procures a solar generation forecast from IHS, which entailed working directly with IHS to define inputs. Energy Efficiency (portion that is not capacity qualified): PJM accounts for energy efficiency in its model by using end-use variables. PJM obtains end-use data from EIA which includes projections of equipment saturation and efficiency. PJM ultimately creates three major equipment indexes: "heating," "cooling," and "other." | ISO-NE has separate working groups to forecast behind-the-meter PV and energy efficiency. ISO-NE forecasts gross load and then incorporates these forecasts. Behind-the-meter PV: The process to forecast PV is informed by input from stakeholders in a separate working group called the Distributed Generation Forecast Working Group. The forecast is a policy-based approach. ISO-NE surveys distribution owners to collect ata on nameplate PV which is installed on their respective systems. ISO-NE then considers the policy goals within each state, and assumes that states will meet their policy goals, e.g. Massachusetts has set forth a program to incorporate 1,600 MW of solar by 2022, so ISO-NE divides the 1,600 evenly in years 2018-2022. ISO-NE then applies a discount factor to account for regulatory uncertainty. After completing the forecast by state, ISO-NE breaks-down the forecast into three buckets (PV which operates in the energy market and is also under obligation in the capacity market; PV which operates in the energy market only, and behind-the-meter PV). The behind-the-meter forecast is backed out of the total PV forecast by subtracting capacity-qualified PV and an estimate for energy-only PV. Distributed PV that is assumed not to sell capacity and is therefore netted out of the peak load before determining capacity requirements. Energy efficiency: The EE forecast is conducted by the Energy-Effieicny Forecast Working Group. The underlying data for ISO-NEs energy efficiency forecast comes form state-sponsored EE program administrators and state regulatory agencies. The forecast is based on average production costs, peak-to-energy ratios, and projected budgets for state-sponsored EE programs. ISO-NE assumes that EE capacity will be bid into (and clear) the capacity market. The base equation utiltized by ISO NE is MWh = [ (1-Budget Modifier) * Budget $ ] / [ $/MWh * Production Cost Increase], and MW = MWh * Peak-to-energy Ratio. Any EE (or "passive DR" as it is termed in ISO-NE) that is assumed to offer into the capacity market is published for information purposes only, and is not subtracted from the capacity requirement. | In the near-term forecast, historical load is adjusted upward to reflect demand response programs and emergency operating procedures, before those values are adjusted for future load growth. The longer-term load forecast accounts for the impacts of energy efficiency programs, building codes and standards, distributed energy generation, and behind-the-meter solar PV. | LSE/EDC Forecasts: While specific methodology is left to each load serving entity, MISO provides guidelines for how to account for DERs. MISO notes that historical load reductions associated with DERs should be added back to historical load values prior to analysis. The reduction of coincident peak caused by capacity-qualified DERs is to be credited separately through the resource adequacy process. LOLE Study: Direct Control Load Management and Interruptible Demand types of demand response were explicitly included in the loss of load expectation model as resources. These demand resources are applied as load reductions in the loss of load expectation simulation before accumulating loss of load expectation or shedding of firm load. | DER projections are created in a botom-up approach. Distributed generation: Distributed generation is created starting from sources such as feed in tariffs, grid code submissions, and other "market intelligence." This is done for 30 technologies, excluding solar. National Grid then conducts scenarios which vary the amount of future distributed generation. Smart grid: There is a module dedicated to residential smart grid reduction. This includes reductions due to a wide variety of drivers, including solar PV, EVs, heat pumps, and different tariff structures. It is based on smart meter roll out, project outcome data from pilots, and percevied customer engagement.
| [Source 1, page 14]; [Source 3] | [Source 3], [Source 4] |  | [Source 3, page 9] [Source 2, page 26] | [Source 1, page 39, 46]
Are inputs from any other entities (stakeholders) voluntary or mandatory? | Electric distribution customers are required to submit official historic hourly load data. Market participants also submit information about significant changes to the underlying load, such as new large consumers (like a server farm or manufacturing plant). | Many inputs are voluntary, as ISO-NE "request" information on PV installations. | It is mandatory that stakeholders provide inputs (outlined above). | Forecasts from load serving entities and electric distribution companies are mandatory | See above.
[Source 2]

## Outputs
| PJM | ISO-NE | NYISO | MISO | UK (National Grid)
How many years? | 15 years | 10 years | Year-ahead for capacity purposes. NYISO Gold Book long-term forecast includes forecasts for 10 years. | Load serving entities submit 10 years of forecasts. The first year is used to set demand in MISO's capacity market mechanism. | Models are run to 2030/31
| [Source 1, page 13] | [Source 2] | [Source 1], [Source 5] |  | [Source 1, page 38]
Granularity of forecast | Daily | Hourly | Annual. Gold Book also reports seasonal (Summer/Winter) | Monthly (for years 1 and 2). Seasonal (Summer/Winter) for years 3-10. | Annual
| [Source 1, page 13] | [Source 2] | [Source 5] | [Source 2, page 34] [Source 3]
How is uncertainty across key variables dealt with? | Weather uncertainty is accounted for with a Monte Carlo approach which considers weather from many previous years and calculates the forercast based on different possible weather outcomes. The simulation creates 12 monthly peak values per forecast per year. The maximum peak demand for each scenario, by zone, then informs the shape of monthly profiles in each season. | Weather uncertainty is accounted for with the creation of an extreme weather 90/10 forecast. The peak load models are estimated with historical data from 2002-2016. The models are simulated with weather data from a 40-year historical period, generating 1000 weekly observations encompassing the mildest to most extreme weather conditions. | Near-term forecast: uncertainty is not reported. Long-term Forecast: Several forecasts are developed to characterize uncertainty. 10/90, 50/50, and 90/10 forecasts are reported in summer and winter periods. Additional forecasts considering only economic variables (without deducted expected efficiency and DER programs) provide an additional range. Reserve Margin Analysis: NYISO uses a Monte Carlo simulation approach to model extreme weather, including a full distribution of peak loads to represent Load Forecast Uncertainty. This uncertainty model considers both weather-driven load forecast uncertainty and economic-driven load forecast uncertainty.Weather uncertainty accounts for 7.9 percentage points of the 18.1 percentage point reserve margin. | LSE/EDC Forecast: Approaches are left to individual LSEs/EDCs, but submitted forecast must represent avarege economic and normal weather conditions. LOLE Study: A load forecast uncertainty model is used to reflect system-wide and zone-specific load forecast error, accounting for the correlation between the two. Historical peak load data are used to estimate the load forecast uncertainty, accounting for both weather and non-weather uncertainty. | Uncertainty is dealt with by creating different weather sensitivities around the base case (low/high wind, cold/warm weather). Scenarios (e.g. "Going Green") are also presented for reference.
| [Source 1, page 13] | [Source 1, page 5] | [Source 6, page 10] | [Source 2, pages 25-27, 36-37]
Are ranges provided (probabilistic vs deterministic), and if so, why? | PJM reports a 50/50 outcome and a 90/10 outcome. | ISO-NE reports a 50/50 outcome and a 90/10 outcome. | Ranges, based on probability distributions of weather variables, are provided in the appendix to reserve margin calculation documents. | LOLE Study: MISO provides load forecast uncertainty (standard deviation) estimates as a percentage of aggregate load | Yes. Ranges are provided for different scenarios and sensitivities.
| [Source 1, page 15] | [Source 2] | [Source 7, page 16]
What sort of reporting is done and how are results presented? | PJM publishes an annual load forecast report which includes zonal-level information with a 50/50 and 90/10 forecast. The report contextualizes the forecasts by discussing a macroeconomic view, including politics and international relations. PJM then discusses its own region more, addressing risks and drivers. PJM provides monthly forecast data by zone in an Excel file available on its website. | ISO-NE publishes the load forecast in its annual CELT report (released in May). The report includes tables with annual energy and peak numbers by capacity year. Along with the base CELT report, ISO-Ne provides hourly forecasts for the next 10 years. ISO-NE also provides information on inputs and on estimated econometric models. | Near term forecast: Results are published on NYISO's website in December of the year before the commitment year. At a similar time, results are also presented in the Installed Capacity Requirement report. Long term forecast: Results reported in an annual report with high-level description of methodology. Both: More detailed discussion of inputs and results is provided through load forecast task force working group materials. | LSE/EDC Forecast: Reported in the long-term transmission plan and reliability assessments. Independent Forecast: Comprehensive report of methodology, inputs, and outputs is issues. LOLE Study: Comprehensive report of methodology, inputs, and results for estimating the system and locational capacity requirements. | Scenarios are presented in the annual "Future Energy Scenarios" report. A separate base case scenario is created for the purpose of an accuracy incentive. This is reported in an "Electricity Capacity Report" document.
| [Source 4] | [Source 2] |  | [Sources 2, 6, 7]

## Accuracy
| PJM | ISO-NE | NYISO | MISO | UK (National Grid)
Is the historical accuracy assessed, and if so, what is reported? | While PJM indicates that it tracks and responds to historical inaccuracy, it does not regularly publish accuracy assesments. However, some accuracy assesments are available in whitepapers, outside the standard annual load forecasting process -- which can be driven by PJM staff's own identification of a need or driven by stakeholder input. In a recent whitepaper, PJM calculated how its model performed on the hottest ten days of prior years. PJM then used actual economic indicators instead of forecasts. PJM then calculated the percent error due to the economic forecast and the percent error due to the modeling not being perfectly specified | The Load Forecast Committee assesses accuracy. While ISO-NE indicates that it tracks and responds to historical inaccuracy, it does not regularly publish accuracy assesments. | The Load Forecasting Task Force reviews the models and considers accuracy each year. NYISO reviews data submitted by transmission owners and municipal electricity systems on a systematic basis to confirm accuracy of submitted data. NYISO conducts its own calculations for respective load and Regional Load Growth Factors. If NYISO finds any input from a stakeholder is significantly different than what NYISO calculates, then NYISO works with the respective stakeholder to reconcile the numbers. | Internally, MISO tracks how the aggregated coincident peak load forecast has compared to weather normalised actual loads. To promote accuracy, as previously discussed, MISO also conducts an in-depth review on a random sample of the forecasts provided by load serving entities. MISO has also commissioned an independent forecast over a three year period (conducted once each year) to assist in an ongoing effort to understand any systematic differences between the current bottom-up forecast approach and alternative top-down forecasting approaches. | National Grid receives a Demand Forecast Accuracy Incentive for the accuracy of its forecast used for capacity planning/procurement. The Incentive is calculated as a currency level multiplied by a measure of accuracy (percentage difference reference - minimum of actual difference percentage or floor / percentage difference reference)
| [Source 3, page 56] |  | [Source 2, page 2-4] |  | [Source 4, page 218]
Do subsequent forecasts take into account response to potential errors? | PJM does not regularly change its forecasts in response to potential errors, though PJM will change its methodology when internal load forecast experts identify a need or when stakeholders initiate a review (that PJM staff or an independent external team may do). | ISO-NE has changed its methodology, such as how it accounts for DERs, but there is no formal process to reassess the methodology on an annual basis | The Load Forecasting Task Force reviews the methodology and updates the approach. The New York State Reliability Council's Installed Capacity Subcommittee also works with NYISO to calculate the reserve requirement each year. The assumptions in the calculations change year-to-year based on new information about weather conditions and about capacity availability. | MISO issues recommendations for how load serving entities should forecast load. These recommendations are updated to reflect best practices. Also, as previously discussed, MISO conducts an in-depth review on a random sample of forecasts. For those forecasts, MISO assesses accuracy and may choose to direct the entity to update the forecast. | Yes. The load forecasting process is dirven by extensive stakeholder engagement and workshops. National Grid has an obligation to publish how it plans to improve its demand forecasting process every year.
|  |  | [source 6] |  | [Source 3], [Source 1, page 57]
Are load adjustments considered, and if so, how? | PJM sends a request to electric distribution companies in mid-July to inquire about large load shifts. The distribution companies may identify the loss/entry of a significant manufacturing enterprise, data center, gas processing plant, or similar manual adjustments that they recommend be made within their territory. PJM then verifies the issue and estimates its impact on peak load. The Load Analysis Subcommittee reviews any adjustments. | As discussed under approach and inputs, several adjustments are made to account for distributed resources and EE (passive DR). | Near term: NYISO requires that load is grossed-up for demand response and emergency operating procedures. The nearer-term nature of the forecast and capacity market means there is generally less of a need for manual adjustments to account for loss/entry of large consumers compared to forward capacity markets. Long-term: adjustments applied for energy efficiency and distributed PV (see inputs tab). | MISO's directions require load serving entities to gross up load for demand-side resources that are qualified for capacity. | National Grid conducts a least worst regret analysis. If the outcome of the model is out of line with National Grid's base case, it may elect to may small adjustments. The government will also make separate adjustments to the implied capacity. Adjustments from the government include adjustments for capacity which does not offer into the capacity market but will remain operational.
| [Source 1, page 3] |  |  | [Source 3] | [Source 1, pages 78-79]

## Sources
Source Number: | PJM | ISO-NE | NYISO | MISO | UK
1 | https://www.pjm.com/~/media/documents/manuals/m19.ashx | https://www.iso-ne.com/static-assets/documents/2017/05/modeling_procedure_2017.pdf | http://www.nyiso.com/public/webdocs/markets_operations/services/planning/Documents_and_Resources/Planning_Data_and_Reference_Docs/Data_and_Reference_Docs/2017_Load_and_Capacity_Data_Report.pdf | https://www.misoenergy.org/Library/Repository/Meeting%20Material/Stakeholder/LOLEWG/2017/LOLEWG%202017%20Charter.pdf | https://www.emrdeliverybody.com/Lists/Latest%20News/Attachments/47/Electricity%20Capacity%20Report%202016_Final_080716.pdf
2 | http://www.pjm.com/~/media/etools/power-meter/power-meter-and-inschedule-submission-deadlines.ashx | https://www.iso-ne.com/system-planning/system-forecasting/load-forecast | http://www.nyiso.com/public/webdocs/markets_operations/documents/Manuals_and_Guides/Manuals/Planning/load_fcst_mnl.pdf | https://www.misoenergy.org/Library/Repository/Study/LOLE/2017%20LOLE%20Study%20Report.pdf | http://fes.nationalgrid.com/fes-document/
3 | http://www.pjm.com/~/media/library/reports-notices/load-forecast/2016-load-forecast-whitepaper.ashx | https://www.iso-ne.com/static-assets/documents/2017/05/2017_solar_forecast_details_final.pdf | http://www.nyiso.com/public/webdocs/markets_operations/documents/Manuals_and_Guides/Manuals/Operations/icap_mnl.pdf | https://www.misoenergy.org/Library/Repository/Communication%20Material/Key%20Presentations%20and%20Whitepapers/Peak%20Forecasting%20Methodology%20Review%20Whitepaper.pdf | http://www2.nationalgrid.com/UK/Industry-information/Future-of-Energy/FES/Engagement/
4 | http://www.pjm.com/~/media/library/reports-notices/load-forecast/2017-load-forecast-report.ashx | https://www.iso-ne.com/static-assets/documents/2017/02/eefwg_16feb17_exhibit.pdf | http://www.nyiso.com/public/webdocs/markets_operations/services/market_training/workshops_courses/Training_Course_Materials/Market_Overview_MT_101/Installed%20Capacity.pdf | https://www.misoenergy.org/Library/Repository/Meeting%20Material/Stakeholder/RASC/2016/20160302/20160302%20RASC%20Item%2004c%20Load%20Forecast%20Review.pdf | https://epr.ofgem.gov.uk/Content/Documents/National%20Grid%20Electricity%20Transmission%20Plc%20-%20Special%20Conditions%20-%20Current%20Version.pdf
5 |  | https://www.iso-ne.com/participate/participant-asset-listings/directory?id=22&type=committee | http://icap.nyiso.com/ucap/public/ldf_view_icap_calc_selection.do | https://www.misoenergy.org/Planning/Pages/IndependentLoadForecasts.aspx | http://www2.nationalgrid.com/WorkArea/DownloadAsset.aspx?id=8589935286
6 |  | https://www.iso-ne.com/markets-operations/markets/forward-capacity-market/fcm-participation-guide/installed-capacity-requirement | http://www.nysrc.org/pdf/Reports/IRM%20Study%20Appendices%202017%20Final.pdf | BPM 11 "Resource Adequacy" https://www.misoenergy.org/Library/BusinessPracticesManuals/Pages/BusinessPracticesManuals.aspx
7 |  |  | http://www.nysrc.org/pdf/Reports/2017%20IRM%20Study%20Report%20Final%2012-2-16%20(002).pdf | https://www.misoenergy.org/Library/Repository/Study/MTEP/MTEP16/MTEP16%20Full%20Report.pdf
8 |  |  | http://www.nyiso.com/public/webdocs/markets_operations/committees/bic_icapwg_lftf/meeting_materials/2016-12-20/2017_ICAP_Final.pdf